## Calculation
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2026-07-30 04:55
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | This spreadsheet is based in an ASHRAE study from the mid 1980's that is documented in the Application Handbook and in the Pocket Handbook. The model is based on commercial office buildings with fire tube boilers, centrifugal chillers, and VAV systems. The spreadsheet simply puts the equation and data from the scan below into an equation to play with electronically.
2 | The basis and limitations of the original 1985 study are scanned and contained on the "original study" tab. You probably should review this info before you use the spreadsheet.
3 | In the current ASHRAE Pocket Guide, the equation appears with the square foot cost adjusted from the original 1983 dollar basis to 1993 dollars. I suspect you could find that in one of the ASHRAE handbooks between then and now also. The current handbook references the data but does not include the details and equations because of the new ASHRAE research and project that created an online maintenance cost and service life databases that can be accessed at the following links.
| Maintenance Cost Data Base | http://xp20.ashrae.org/publicdatabase/maintenance.asp
| Service Life Data Base | http://xp20.ashrae.org/publicdatabase/service_life.asp
2 | I added the inflation adjustment factor since the lastest version of the equation I have is based on 1993 dollars. To adjust, I use an inflation calculator that you can access on line at the link below. You can see the result I use on the tab "Consumer Price Index".
http://www.bls.gov/data/inflation_calculator.htm
Instructions
To use the spreadsheet, fill in the following information in the cells below:
Enter the building age in years into the lavender shaded cell
Link to the appropriate heating system adjustment factor in the red cell using the table to the right if the heating system is not fire tube boilers
Link to the appropriate cooling system adjustment factor in the blue cell using the table to the right if the cooling system is not centrifugal chillers
Link to the appropriate distribution system adjustment factor in the blue cell using the table to the right if the distribution is not VAV air handling
Add an inflation adjustment based on the consumper price index in the orange cell
The result in cents per square foot and dollars per square foot show up in the yellow cells
Calculation
| Total Maintenance Cost in cents per square foot = | (Base Cost + (Age adjustment factor x Age in years) + Heating system adjustment factor + Cooling system adjustment factor + Distribution system adjustment factor) x Inflation Adjustment
| Base Cost - | 48.4 | cents per square foot | Heating Equipment Adjustment Factor (cents per square foot, 1993 dollars)
| Building age in years - | 1 | years
| Age adjustment factor - | 0.18 | (from ASHRAE research) | Water tube boiler | 1.12
| Heating system adjustment factor - | 0 | cents per square foot | Cast iron boiler | 1.36
| Cooling system adjustment factor - | 0 | cents per square foot | Electric boiler | -3.87
| Distribution system adjustment factor - | 0 | cents per square foot | Heat pump | -14.05
| Inflation adjustment - | 1.48 | (Consumer price index calculator) | Electric resistance heat | 19.29
| Annual Maintenance Cost = | 71.8984 | cents per square foot | Cooling Equipment Adjustment Factor (cents per square foot, 1993 dollars)
|  | 0.71898 | dollars per square foot
|  |  |  | Reciprocating chiller | -5.8
|  |  |  | Absorptoin chiller (single stage) | 27.91
|  |  |  | Water source heat pump | -6.84
Distribution System Adjustment Factor (cents per square foot, 1993 dollars)
|  |  |  | Single zone | 12.02
|  |  |  | Multizone | -6.67
|  |  |  | Dual duct | -0.42
|  |  |  | Contant volume | 12.77
|  |  |  | Two-pipe fan coil unit | -4.02
|  |  |  | Four-pipe fan coil unit | 8.41
|  |  |  | Induction unit | 9.89